TEL: (203)-634-3900   FAX: (203)-238-2425

EMAIL: HIGHPOWER@HIGHPOWERSECURITY.COM

WEB: WWW.HIGHPOWERSECURITY.COM

If you are having problems using this product, please call Highpower Technical Support 
at 203-634-3900.  We are here to help and we appreciate your business!

MODEL 8000 DOOR CONTROLLER WITH POWER OVER ETHERNET (POE)

HARDWARE MANUAL WITH HMS SOFTWARE V4.2

DOCUMENT VERSION 1.1

DOCUMENT PART NUMBER: 980-8000-1.1.0

TABLE OF CONTENTS

CONTROLLER DESCRIPTION	2

KEY FEATURES	3

8000 CONTROLLER BOARD	4

BOARD PHOTO AND LAYOUT	4

BOARD CONNECTIONS BLOCK DIAGRAM	5

NOTICE OF INSTALLER QUALIFICATION	6

POWER REQUIREMENTS	6

FLEXIBLE POWER SUPPLY OPTIONS	6

DETAILS ABOUT POWER OVER ETHERNET FEATURE	6

STAND ALONE OPERATION	6

ADDITIONAL I/O FEATURES	7

STAND-ALONE OPERATION DETAILS	7

DESCRIPTION	7

SCHEDULES	7

REAL TIME CLOCK	8

ADVANCED STAND-ALONE FEATURES	9

SOFTWARE INTERFACE	9

SCHEDULING PROGRAMMING	9

AUTOMATIC UNLOCKING USING SCHEDULES	10

HOLIDAYS	12

FIRST-PERSON-IN FEATURE	13

FORCED LOCKDOWNS	13

FORCED DOOR UNLOCK (PASSAGE MODE)	14

NORMAL DOOR OPERATION	14

STAND ALONE FEATURES WITHOUT SOFTWARE CONTROL	14

WHEN A CONNECTION TO A PC IS NOT AVAILABLE	14

LOCAL ENROLLMENT (PROGRAMMING EACH READER WITHOUT SOFTWARE)	15

OPEN ENROLLMENT MODE	15

PROGRAMMING CONTROL CARDS	16

HARDWARE FEATURES	17

ON BOARD JUMPER FUNCTIONS	17

REMOTE RELEASE	18

READER PORTS	18

ADVANCED READER PORT FEATURES	18

PROXIMITY (WIEGAND) FORMATS (BOTH READER PORTS)	19

DETAILS ABOUT USING WIEGAND DATA	19

READER PORT 1 SPECIAL FEATURES	21

BARCODE SYMBOLOGY SUPPORT	21

MAGSTRIPE INPUT	21

DETAILS ABOUT BARCODE INPUT	21

PDI MODE	22

BARCODE NORMALIZATION	22

MASKING INPUT DATA	22

CUSTOM WIRING DIAGRAMS AND UNIQUE APPLICATIONS	22

TROUBLESHOOTING ISSUES	22

WARRANTY INFORMATION	22

APPENDIX A – MEMORY RECORD SIZE CALCULATIONS	23

APPENDIX B – COMPATIBLE POE SWITCHES	23

APPENDIX C – WIEGAND BIT SIZE TABLE	24

APPENDIX D – TESTED COMPATIBLE READERS	25

PROXIMITY READERS	25

BAR CODE READERS	25

MAG-STRIPE READERS	25

# CONTROLLER DESCRIPTION

The 8000 Series is a door controller designed for one or two door operation.  It provides the installer with the latest advancements in Ethernet communications and Power-Over-Ethernet technology.  The 8000 controller has been specifically designed for use with the Highpower Management System (HMS), which is a SQL based database and control program for the Windows .NET platform.   The 8000 can also run in stand-alone configurations without software.  When using the HMS software the 8000 is networked to provide a rich control environment that allows customers to manage alphanumeric card IDs, schedules, and holidays and to generate reports based on system activity.

The 8000 controller is used in conjunction with external card reader(s) to create a secure two-piece access control solution.  The card reader inputs of the 8000 controller support a wide variety of reader types including:

- Barcode readers (Wiegand Data on Port 1 or Port 2 or Un-encoded Barcode Data on Port 1)

- Proximity Readers (Wiegand Data on Port 1 and Port 2)

- Magnetic Stripe Readers (ABA Data on Port 1 and Port 2)

- Wiegand Card Readers  (Wiegand Data on Port 1 and Port 2)

Communications from the controller to the HMS software is accomplished through either RS-232 port (serial) or more commonly through the built-on Ethernet port, which supports the 802.3af POE standards.

The Power-Over-Ethernet features of the controller are unique in that the controller allows the installer to power the controller itself, two card readers and two electric strikes simultaneously when the total current draw of the connected devices is fewer than 700mA @ 12VDC (around 9 Watts).

This document will describe the features of this controller for simplified installation and setup.

# KEY FEATURES

- RS-232 and Ethernet Networking with 802.3af Power-Over-Ethernet built on board.

- Two-Door Operation with Request to Exit and Door Position Switch monitoring.

- One-Door model available.

- Flash-Based Non-volatile memory 512K for each reader.

- 25 Schedules with 8 periods (when used with HMS software).

- Automatic door unlocking and relocking cycles.

- Adjustable memory structure – Memory structure is adjusted based on length of longest user ID in order to maximize memory space for IDs (automatically configured when using HMS software).

- Reader inputs can be configured to accept different signal types including Wiegand and ABA.  Reader Input 1 can also accept barcode symbologies (including Code 3 of 9, I 2 of 5, Interleaved I 2 of 5, Codabar, UPC A, EAN13 and Code 128 barcode types).

- Reader inputs can mask data to include or exclude digits from user ID on a hardware level.

- Online or Offline modes of operation.  Offline mode is used when using controller with HMS software.

# 8000 CONTROLLER BOARD

## BOARD PHOTO AND LAYOUT

## 8000 BOARD CONNECTIONS BLOCK DIAGRAM

# NOTICE OF INSTALLER QUALIFICATION

The items listed in this manual may require the services of an individual who is trained in the application and installation of life safety equipment.  All wiring must be in compliance with current NEC guidelines.

# POWER REQUIREMENTS

## FLEXIBLE POWER SUPPLY OPTIONS

The controller is powered using either 12VDC connected to one of the terminals on the board (12vdc IN or ac adapter IN) or through using Power-Over-Ethernet via the Ethernet connector.

There is internal voltage regulation on the controller board, so a 13.8 Volt supply, or an unregulated / or regulated plug in wall adapter that can provide the required power is acceptable to use.

8000 Controllers equipped with the POE feature can get power directly through the CAT 5 networking cable through a POE network switch, so a local power supply is typically not required.

The controller power requirement (for the board only) is:

Without Onboard Ethernet: 150 mA @12 VDC

With Onboard Ethernet: 350 mA @12 VDC

## DETAILS ABOUT POWER OVER ETHERNET FEATURE

The 8000 is fully IEEE 802.3af compliant.  Power can be supplied over the Ethernet data lines, or on one of the unused pairs.  Normally, the power is supplied by an Ethernet switch but it can also be supplied by a power inserter. A list of tested and recommended power inserters can be found in the appendices.

When using POE, the typical installation will require installing either a POE switch or a power inserter near the Ethernet switch. Category 5 cable can be used to connect to the controller board for lengths of up to 100 meters.

Battery backup can be implemented by using a UPS at the switch or power insertion point instead of traditionally having a battery backup at each controller box. There is no need when using POE to provide battery backup at the controller location. It is highly recommended that you install a UPS on your switch equipment to insure constant uninterrupted controller operation.

Note that an 8000 controller with POE does not have to be powered over the Ethernet. You can still power it with a standard supply. If you intend to use POE but cannot initially install the POE switch or power inserter, the 8000 can still be installed using a power supply temporarily. The 8000 should not be connected to a POE source and a local power supply at the same time. Doing this could damage the controller.

You can power small external devices directly from the POE interface by setting appropriate jumpers. The power insertion jumper(s) must be on for the POE power to pass through the output relay. See the jumper configuration section below for setting the appropriate jumper settings.

# STAND ALONE OPERATION

The stand-alone mode operates without the need of a real-time computer connection. This is the mode that the controller is typically configured to and this mode is used in conjunction with the HMS software.  When a card is read, the controller searches for the card number in it’s memory.  If the card number is found and the card’s schedule is valid, access is granted.  Cards are normally entered into the controller by transferring the card data from a PC.  You can, however, enroll the cards locally at a connected reader using control cards.  If cards are enrolled locally, there is no need for a computer connection at all other than for the initial programming.

There is an audit trail feature in the controller while operating in the stand-alone mode. Whenever a valid card is read, the card number, along with the date and time, is stored in the controller's memory. This audit trail data can be transferred to a computer at any time and is automatically retrieved when using the HMS software. Optionally, cards which are read, but not granted access, can also be stored in the audit trail if you wish, to log invalid entry attempts. Audit trail data is stored in non-volatile flash memory and is not lost if power is lost.  A separate audit trail is stored for each of the two doors (readers).

When a valid card is found, the appropriate output relay is triggered for the pre-programmed time, allowing the door to be opened.  When the door is closed, the controller can automatically re-lock the door rather than wait until the full time period has elapsed (anti-tailgating feature) when the controller is used in conjunction with a Door Position Switch (DPS). Anti-tailgating is a programmable option.

The controller supports scheduling in the stand alone mode. Schedules tell the controller which time of day a card has access for.  A card number can be associated to one or a series of schedule times, allowing multiple access times during an individual day.  When using the HMS software, 25 schedules are provided, each schedule having 8 periods.

## ADDITIONAL I/O FEATURES

A "Request to exit" switch can be connected to an input on the controller for remote door unlocking. When the switch is engaged, the controller will trigger the relay for the pre-programmed time, allowing the door to open. The Request to exit can operate in both modes, stand-alone and online.

# STAND-ALONE OPERATION DETAILS

## DESCRIPTION

Stand-alone mode is the most commonly used mode in the controller.  This mode is used by the HMS control software.  In the stand-alone mode, the controller operates independently from a computer, but allows a computer to make changes to the controller memory.

All card numbers which have access through the door must be loaded into the controller's memory. This can be done either by loading in the data from a PC, or by enrolling each card at the reader locally. The preferred method will depend on the number of cards that you need to enroll and whether you want to use the scheduling features provided in the controller. Cards which are enrolled locally at a reader cannot use the scheduling features, so if you need to use schedules then card data must be downloaded into the controller via software.

The number of cards that can be stored in the controller depends on the size of the cards. Memory in the controller is pre-allocated and therefore you can adjust the number of allowable cards in the system based on your card data size. A list of the total number of cards which can be stores is provided in the Appendices.

## SCHEDULES

In the stand-alone mode, schedules are supported in the controller.  Schedules allow you to specify the times of day that an employee has access for. There are 199 unique schedules that can be programmed into the controller, each schedule representing the allowable times for employee access for 7 days (Monday thru Sunday).  When using the HMS software, these 200 schedules are grouped into schedules and periods, allowing for 25 schedules each with 8 periods (shifts).

Holiday schedules can also be entered in. The holiday schedule in the system is loaded in as day “8”.

Cards which are enrolled at a reader are enrolled with no schedule, meaning they will have access at all times. This means that if you enroll cards at the reader you cannot specify a specific schedule.  Currently, you should not use the enrolling feature at the reader if you are also using the HMS software.

Each schedule specifies the start time and end time that access is allowed.

As an example, 0700 thru 1529 represents 7:30 in the morning till 3:29 in the afternoon. At 3:30 in the afternoon and after, the employee will not have access.

It is possible to associate schedules in the controller. When you associate schedules, you are linking multiple schedules together.

For example, let us say that you want to allow access between 7 in the morning and noon, and then again between 1 pm and 4 pm. You would enter in two different schedules in the system, one for the 7 to noon, and another from 1 to 4, and then link them together. The result is a schedule which allows access from 7 to noon, and then from to 4. From noon until 1259, access is not allowed.  When using the HMS software, the software will link sets of 8 schedules together automatically to form 25 schedules each with 8 intervals (shifts).

There is an audit trail in the controller which will record each transaction that occurs in the reader. The audit trail can be turned on or off. Whenever a card is read, the date and time, along with the card data is stored in the audit trail. This data can be retrieved from the controller at any time.  This audit trail data is stored in a circular buffer to prevent the latest audit information from getting lost if the audit memory space is full. Note that there are separate audit trail logs for each reader connected to the controller.  The HMS software will retrieve this audit trail information for each reader and use the information to generate reports with the HMS reporting facility.

## REAL TIME CLOCK

The time is set in the 8000 using the HMS software or via typed command.  Time is accurate to about 1 minute per year.  It is suggested that you update the time on a periodic basis.  The real time clock is updated every second. Schedule times, holiday periods, and other real time events are also checked every second.  Audit trail data is accurate to the second.

To set the current time in the system using the HMS software, right click on the controller that you wish to set the time on.  Left click on “Set Clock”.

HMS allows you to set the clock to different times which is important if the Controllers are in different time zones:

# ADVANCED STAND-ALONE FEATURES

## SOFTWARE INTERFACE

Adding cards and changing settings in the controller is mainly done using the HMS software.  You do have the option however, to add cards to the controller by using control cards.  In doing this, you do not need software for programming, but you will not be able to easily use the advanced scheduling and other advanced features of the controller.

## SCHEDULING PROGRAMMING

The controller contains memory for the loading of up to 199 schedules.  These are identified as schedule numbers 001 through 199.  Each loaded schedule consists of 8 entries total.  Seven schedules for the 7 days of the week and 1 entry which is used for holidays.  Each entry contains a start time and an ending time that access is allowed for. If an entry for a particular day is not entered, then access is not allowed for that day.  The HMS software automatically groups these 200 schedules into 25 schedules each with 8 intervals (shifts).

Entered schedule times are inclusive, not exclusive. If you want to allow access from 7 in the morning until noon (don't allow access after noon), then the entered times are 0700 thru 1159. This means that at 1159 you can still unlock the door, but at 1200 noon you cannot. To refer to midnight, you use 0000.

Schedules cannot cross midnight. To cross midnight you enter in a time period for the first day, and then a time period for the second day. In order to allow two time periods in the same day, you must associate two schedules together.  This is handled automatically when using the HMS software.

Schedule 0 is a reserved schedule. This schedule is an open schedule, meaning access is allowed at all times. Any card number entered into the system with schedule 0 is automatically allowed access at all times, all days, including holidays. Cards which are enrolled locally at the readers are also entered in with schedule 0. This means they have access at all times.

## AUTOMATIC UNLOCKING USING SCHEDULES

The 8000 contains a feature to allow either door to be unlocked during specific times of the day. You may want, for example, to keep the door open during shift changes, or during lunch periods.  The HMS software can use your scheduling information to lock and unlock the doors automatically.

Schedule number 200 is a special function schedule in that the controller will automatically unlock the door when the schedule time starts for that particular day.  HMS will associate multiple schedules together (starting with schedule 200) in order to unlock the door for multiple periods of the day.

During the unlock period, card scans are still allowed, but they have no effect on relay operation since the relay is already actuated. If the audit trail is being used, the card scans will be stored as usual.

The unlock schedules will optionally work on holidays using the "day 8" schedule times. At the beginning of the holiday period, the relay is automatically locked as usual, and then unlocked when the schedule 200, day 8 unlock start time is reached.

Adding a schedule with the HMS software is accomplished by right clicking on Schedule in the configure tree and selecting “Add a Schedule”.

Once you have clicked Add a Schedule, then the schedule screen pops up, which allows you to set up your schedule times:

Once you have configured your schedule, you must tell HMS to use the schedule as an unlocking schedule.  To do this, right click on the door that you wish to work on an unlock schedule and select “Properties”:

Once you click on properties, the door properties window will be shown.  Pick the schedule that you have created to use as an unlock schedule:

Once you select “OK” the doors will work on the selected unlock schedule once the system has been Synced.

Note that Unlock periods are not implemented if the system is in a Forced Lockdown or Forced Open mode (described in later section).

## HOLIDAYS

The controller supports both recurring holidays and non-recurring holiday periods.  Recurring holidays are holiday periods that recur for the same date every year (like New Years Day or Christmas).  Non-recurring holidays do not recur from year to year, or the dates change, and therefore need to be programmed in every year (Special events, Labor Day, etc).

During a holiday period, the controller automatically turns off the relay, and switches to the day 8 schedule.  Day 8 is therefore considered the "holiday schedule".  During the holiday schedule, even if an employee normally has access for that specific day, he will not have access unless access is permitted under the day 8 schedule or if he has been entered in with schedule 0, which allows access at all times.

Non-recurring and Recurring holiday periods are specifically handled in the configure tree of the HMS software.  Right-click on either “Event Holidays” or “Recurring Holidays” in order to Add a holiday to the system:

## FIRST-PERSON-IN FEATURE

First-Person-In is a feature which allows a door unlock period to be delayed until at least one valid card is read. This function is normally enabled to make sure that if the door is to be unlocked, that there is at least someone around when it does unlock.

If the First Person In option is turned on, then when an unlock period is scheduled to start, the door will remain locked. When the first valid read occurs, the door is then unlocked and remains open until the end of the unlock period.  A valid read is any card which normally would have been accepted if the system was not in the unlock period.

The first-person-in features is specifically handled in the configure tree of the HMS software.  In HMS, right click on the appropriate door in the configure tree, select “Unlock Schedule Modes” and then click on “Don’t unlock this door until a valid swipe occurs, then leave the door unlocked.”

To disable the First-Person-In feature, select “Unlock the door immediately at the start of the unlocking schedule.

## FORCED LOCKDOWNS

Either door connected to the 8000 can be locked down at any time using the HMS software, and also with the reading of a special lockdown card.  During the lockdown period, only cards entered in with a schedule 0 will have access.

The forced lockdown can be turned off using the HMS software or also by scanning in the "End forced mode" control card.

In the HMS software, right click on the appropriate door in the configure tree, select “Forced Door Modes” and click “Keep Door Locked (Lock Down Mode)”.

## FORCED DOOR UNLOCK (PASSAGE MODE)

Passage mode (Forced "opens" of the door) can be achieved using the HMS software or by presenting the "force open" control card to a reader.  In the HMS software, you right click on the appropriate door in the configure tree, select “Forced Door Modes” and click “Keep Door Unlocked”.

The door will remain open until the door is put back into either normal operation or into a forced lockdown.   An "End forced mode" card can also be scanned to enter forced lock open mode.

## NORMAL DOOR OPERATION

Normal door operation returns a particular door to normal operation from Forced Lockdown or Passage Mode.  The door will resume operating with schedules and operating with valid cards.

In the HMS software, you right click on the appropriate door in the configure tree, select “Forced Door Modes” and click “Resume Normal Door Operation”.

# STAND ALONE FEATURES WITHOUT SOFTWARE CONTROL

## WHEN A CONNECTION TO A PC IS NOT AVAILABLE

The following features provide basic ways to use features of the controller without connecting to the HMS software package.  These modes are usually reserved for customers with special application requirements.

## LOCAL ENROLLMENT (PROGRAMMING EACH READER WITHOUT SOFTWARE)

Local Enrollment is the process of loading cards into the controller locally at the reader.  When you enroll cards at the reader, they are entered into the controller without schedule information, meaning that the locally enrolled cards will be active at all times.

In order to enroll locally, you must start the enroll process by reading a control card for local enrollment.

There are four control cards for local enrollment:

• Add Control Card		Start adding cards

• Delete Control Card		Start deleting cards

• Clear Control Card		Clear all cards in memory

• End Control Card		End the add or delete sequence

You first scan the Add card if you want to add cards.  All cards presented after the add card will be added into the controller memory, until you present the End card.

To delete cards you follow the same sequence but use the Delete card rather than the add card.

The Clear card should be used with caution and is used to delete all cards in the system.

Note that these control cards Add, Delete, and Clear only the memory allocated to the specific reader that you are using. If you have a 2 door controller and delete a card on one reader, it will also need to be deleted from the other reader as well. The same applies to adding cards.

You do not need specially made control cards for programming. The four control cards that you use can be any four cards of your choosing. You can put the controller into a "learn" mode, where it will learn the four control cards that you read, and designate these cards as control cards. For more information on this feature refer to the section Learn Mode - Programming Control Cards.

During the add process, the LED (in the reader) will blink slowly. During the delete process, the LED will blink quickly. A single beep from the controller means that the card has been added or deleted. A double beep means that the card has not been added or deleted.  The above applies to readers with 1 bi-color LED. If you are using a reader with two LED's connected, then the 1st LED blinks slowly or quickly, and the 2nd LED is used as an acceptance indicator.

## OPEN ENROLLMENT MODE

Open Enrollment is a special mode which allows the controller to treat all wiegand input data formats the same. No matter what the format, the controller will accept the format and append zero bits to the data to make it a 64 bit stream. The data is stored internally in the controller as 64 bits. If you upload this data, or transmit the data in real time mode, the data is sent as 16 hex characters.

Note than when in the open enrollment mode, you can enroll the cards either at the readers, or alternatively upload/download them using a command typed to the controller through a terminal.

When the controller is in this mode, only wiegand data is affected. Magstripe data and barcode data can still be entered along with the open enrollment wiegand data.

One caveat when using this mode is that the record length must be set to a minimum of 8 digits, which is the data length required for open enrollment.  You should not be using the HMS software in conjunction with the Open Enrollment Mode.

## PROGRAMMING CONTROL CARDS

There are seven control cards which can be programmed into the controller. These cards are:

- Add Control Card (Card 1)

- Delete Control Card (Card 2)

- Clear Control Card (Card 3)

- End Control Card (Card 4)

- Lockdown (Card 5)

- Force Open (Card 6)

- End Lockdown / Force Open Modes (Card 7)

To identify the control cards that you want to use to the system, you must place the controller into Learn Mode.  To do this, you remove jumper 1 on the controller board and recycle power. The controller will now be in Learn Mode.  The bi-color led on the board will alternate between red and green, and the led on the reader will blink quickly.

At this time you can read in the first 4 control cards, or all 7 (if you want to implement the Forced Lockdown and Forced Open control card features).

When you are done, turn the controller power off, put jumper 1 back on, and then restart the controller.  The controller will now identify these cards as control cards.

Upon reading each card, the controller will beep three times acknowledging that it has read the card.

Note that barcode and magstripe control cards greater than 16 characters in length are truncated to the first 16 when used as control cards. Wiegand / proximity control cards can be any format, up to 64 bits.

Also note that you will not have to present cards 5, 6, and 7 are not required if you are not using those modes.

# HARDWARE FEATURES

## ON BOARD JUMPER FUNCTIONS

| JUMPER | FUNCTION |
| --- | --- |
| JP1 | When removed and powered up, controller enters “Learn” mode. |
| JP2 | RS-232 or USB active port selection (on models with USB). |
| JP3 | TCP/IP or RS-422 active data port selection (on models with TCP/IP). |
| JP4 | Selects which port data is sent out to in online mode. On selects (TCP/IP/RS-422). Off selects (RS-232/USB). |
| JP5 | Used to place the RS-232 port into a known state. Forces the controller to start up with the RS-232 port set at 9600 baud, 8 data bits, no parity. Remove this jumper and power up to make the RS-232 the online port with the above settings. Used when the ports have been changed to some unknown state. |
| JP6 | Both of these jumpers should be on in order to provide 5V power to the readers. JP10 should be OFF when these jumpers are connected. |
| JP7 |  |
| JP8 | Reserved for future use. THEY MUST BE LEFT OPEN. |
| JP9 | Reserved for future use. THEY MUST BE LEFT OPEN. |
| JP10 | Used to connect 12V power to the reader outputs. JP6 and JP7 must be removed when JP10 is connected. |
| JP11 | Jumper supplies power from the POE supply directly to the common terminal of Relay 1. When open, Relay 1 works as a dry contact set. Do not use with inductive loads. |
| JP12 | Jumper supplies power from the POE supply directly to the common terminal of Relay 2. When open, Relay 2 works as a dry contact set. Do not use with inductive loads. |

## REMOTE RELEASE

The Remote Release Terminals provide a connection for external switches that are used to trigger Timer 1 or Timer 2.  By activating these timers, the external switches can be used for the remote release of Door 1 or Door 2.

NOTE: When using the Remote Release feature, make sure to enable the remote release by setting the corresponding Remote Release Jumper (JP3 or JP4).

## READER PORTS

The controller has two Ports for reader connection.

Led Control Lines change the state of the LED on the Wiegand Device.  The LED on the first Wiegand Port indicates the state of Relay Output 1.  The LED on the second Wiegand Port indicates the state of Relay Output 2.

# ADVANCED READER PORT FEATURES

Both reader inputs of the 8000 support Wiegand and ABA.  Reader input 1 additionally supports barcode symbologies.  Readers can use either 12VDC or 5VDC power and can be powered off the controller in both powered mode and using POE.  Power is supplied directly from the controller for the readers.

The 8000 supports the connection of an undecoded barcode reader directly on the reader #1 connection ONLY. It you have a 2-door controller, and need barcode reading for both doors, a decoded barcode reader with magstripe emulation or wiegand interface, can be used for the 2nd reader or for both readers.  Contact Highpower for assistance when picking readers with a barcode input.

Wiegand and Proximity readers should have a standard Wiegand data output (Data 0 and Data 1 signals).  Most, but not all, proximity readers have this type of output.  Compatible models include readers from many popular brands including and reader from Farpointe Data, HID Corporation, Indala and AWID.  Barcode readers include readers from International Bar Code (IBC).  The inputs of the 8000 have been tested with the Farpointe Data reader line specifically.  Highpower can provide you with a Farpointe reader for your application.

Magnetic stripe readers should have an undecoded magstripe output, known as "clock and data" signals. If you need a dual-technology single reader, then any of the Magbar or Smart Prox readers from International Barcode, with ABA, Wiegand, or wand emulation outputs can also be connected to the controller.  Multiple readers may be connected to the same reader input, as long as the readers have open collector outputs. If this multiple readers on one port is used, only one reader can transmit to the controller at a time.

Most 8000’s are in the two-door configuration.  The 2-door controller supports the connecting of 2 separate readers. Each reader is treated individually and operates independently of the other. In the stand-alone mode, each reader uses it's own memory space for accessing valid id's, and for the audit trail. In the online mode, both readers share the same output.  Reader styles can be mixed. You do not have to use the same technology reader on each input. For example, you can have a barcode reader as reader #1, and a magstripe reader as reader #2, or you could combine magstripe/proximity readers, etc.

## PROXIMITY (WIEGAND) FORMATS (BOTH READER PORTS)

The controller supports all proximity and wiegand data formats up to 64 bits. Each individual field (site code, id number, and optional issue code) is extracted and converted to a decimalized number, resulting in a numeric string. This is the string that is used for comparisons in the controller while in the stand-alone mode. In the online mode, this string is simply transmitted. The controller converts this information into a string so that masking of the data can be achieved easily should you need to mask out numbers from the card ID.

A special mode of the controller called open enrollment allows you to accept wiegand data without a decimalized conversion.  In this mode, all wiegand formats up to 64 bits are accepted and stored directly with no conversion.

Three different formats are programmable, allowing the controller to accept three different card formats for each reader.  Each format is fully configurable by bit, and the extracted data can be modified by the controller prior to comparison or transmission.  Numbers can be added to the data, or deleted from the data. See the Advanced Concepts section for more information on this topic.

## DETAILS ABOUT USING WIEGAND DATA

The controller will accept any size wiegand input up to 64 bits. Please note that most proximity readers output data in the Wiegand data format.

Because Wiegand data is binary, the data is normally meaningless unless it is decoded into a useful number in some way. The industry standard for wiegand data is a 26-bit stream, consisting of a site (facility) code of 8 bits and also a badge (id) number of 16 bits. This is also the default setting for the controller. The largest site code that can be transmitted with 26 Bit Wiegand is value 255.  The largest ID code that can be transmitted in 26 Bit Wiegand is 65535. The controller therefore decodes 26 bit wiegand numbers into an 8 digit string, consisting of 3 digits for the site code, and 5 digits for the id number, by default.

In order to decode a different format, you must program the controller so that it understands the bit structure that you will be reading. It is necessary to do this so that the controller will end up with the correct unique id number. You must program in the starting bit position and number of bits for the site code (if it is being used), as well as the id number. Issue codes are also supported as a separate field and they can be decoded or ignored.

It is important to note that the controller always processes wiegand bit fields in the order of site, badge (id), and then issue code (in the rare case where an issue code is being used).  The controller will accept any size wiegand input up to 64 bits.

When decoding numbers are read from the card, the controller will concatenate each of the three fields in the order of site, badge, and then issue to create the actual card data number that is stored in the controller.

For example, if you have a proximity card with a facility code of 33 and an ID of 12, and have programmed the controller to decode the site code to a 3 digit number, the id field to a 6 digit number, and to ignore the issue code, the resulting number after decoding will be 033000012.

You can program the controller to accept up to 3 different wiegand data formats, and decode them based on the parameters you have set. It is therefore possible to mix different wiegand or proximity cards together in the controller. The controller will automatically discriminate them based on their bit lengths.

It is also possible to mask the wiegand input (omit or add numbers in certain positions from the read results). Characters can be added to or deleted from the decoded number using one of the input masks (described later).

Backward bit structures may also be handled by the controller. Some proximity cards contain site codes and id fields that are encoded backwards with the least significant bit first, rather than last. It is possible for the controller to read these bit streams and decode the proper number.

## READER PORT 1 SPECIAL FEATURES

### BARCODE SYMBOLOGY SUPPORT

The 8000 controller supports Wiegand and ABA (also called clock-and-data) on both reader ports.

Additionally, Reader port 1 has some additional unique features in that it can also read unencoded barcode signals.  The controller supports barcode symbologies through reader port 1 only.  The following barcode symbologies are supported:

- Code39

- Interleaved 2 of 5

- Industrial 2 of 5

- Standard 2 of 5

- Codabar

- UPC A

- EAN 13

- Code 128

The maximum number of barcode characters that can be decoded by the controller is 22. This includes start and stop characters and check digits.  The controller can be programmed to auto-discriminate Kronos barcodes, which are normally 17 or 18 digits long. In this mode, the id is extracted from the entire Kronos string, and the remaining information is ignored.  The controller can also be programmed to extract the PDI from a military/CAC barcode. This extraction yields a 9 digit number (typically the SSN).  There are a number of programming options that affect the way barcodes are read and processed. These options can be found under the Advanced Concepts section.  Barcode data can also be masked (omission of digits in barcode) and reformatted (numbers added to the string) on the hardware level.  Note that the controller supports the direct connection of an undecoded barcode reader ONLY ON READER PORT 1.

### MAGSTRIPE INPUT

Both the Track 1 and Track 2 character sets are supported by the controller.  Separator character translation is also supported, as well as B and C start sentinels for the Track 2 character set.  Note that magnetic stripes on tracks normally use the Track 2 character set and is fully supported.

Magnetic stripe data can also be reformatted using the masking commands (see Advanced Concepts).

### DETAILS ABOUT BARCODE INPUT

The controller can decode numerous barcode symbologies. For all supported symbologies, it is possible to prefix and suffix barcode data with up to 5 characters. This prefix and suffix is in addition to the ability to add and delete characters via the masking commands.

Start and stop characters may also be included, along with check digits and scan direction indicators. These items are normally only used when in the online mode; however they can be used in the stand-alone mode as well.

The controller also has advanced barcode decoding options, which are useful when there is writing before or after the barcode, or there are extraneous bars in the barcode.

### PDI MODE

When using the 8000 on Port 1 with an unencoded reader, the 8000 can automatically extract the PDI from military and Common Access Card (CAC) barcodes. The PDI is extracted to a 9-digit number. This number, on most cards, is the user's SSN.

### BARCODE NORMALIZATION

In rare cases, if you are reading barcodes, you may have information on the card immediately to the left or right of the barcode, which can interfere in the controller's ability to automatically decode the barcode. The 8000 has an option for you to "normalize" the barcode, by selecting which part of the data is to be decoded as a barcode.

## MASKING INPUT DATA

The 8000 supports a number of masking parameters, including character insertion, deletion, and selection. Character insertion allows you to add any sequence of characters to the input data at any location. Character selection allows you to select only those characters that you want. Unselected characters are deleted. There are separate masking tables for each type of input.

For example, if you are using 2 different sets of proximity cards, 26 bit and 34 bit, with different site codes on the 34 bit cards than the 26 bit cards, and want to keep the site codes the same, you can program the controller to ignore the site codes on the 34 bit card, and then use the masking commands to add in the appropriate site code so that the site codes are the same as the 26 bit cards.

# CUSTOM WIRING DIAGRAMS AND UNIQUE APPLICATIONS

Highpower can provide design services for you application including wiring diagrams, installation procedures, and system integration.  We offer turnkey solutions for your security requirements.  Please feel free to contact Highpower directly for integration services.

# TROUBLESHOOTING ISSUES

This section describes troubleshooting information that is discovered through technical support calls with our customers.  Highpower attempts to update this section on a regular basis with solutions to commonly asked technical support questions.  Contact Highpower at 203-634-3900 with technical questions.

| Problem Description | Resolution |
| --- | --- |
| Nothing currently reported. |  |

# WARRANTY INFORMATION

Thank you for choosing a Highpower product!  The Highpower Security Products, LLC Door Controller Model 8000 is manufactured to the highest quality standards to provide years of dependable service.  The Model 8000 is warranted for one year from the date of shipment against defects in parts, workmanship and materials, when installed in accordance with instructions.  Defects that occur within this warranty period, under normal use of the product, shall be repaired or replaced with a new unit, solely at our option.  Warranty is void when product has been modified, damaged, abused, misused, subjected to abnormal use or neglect, or subjected to harsh operating environments out of the normal operating specifications.

No agent, employee or representative of Highpower Security Products, LLC has authority to bind Highpower Security Products, LLC to any oral affirmation, representation or warranty, other than set forth above.  Highpower Security Products, LLC expressly disclaims all other warranties, expressed or implied, including but not limited to any implied warranties of merchantability or fitness for a particular purpose.  “Fair-Safe” and “Fail-Secure” are definitions only.  Use of these terms is not a performance warranty, but merely a descriptive term used to characterize a design feature.

## APPENDIX A – MEMORY RECORD SIZE CALCULATIONS

This appendix lists the number of available slots in the unsorted memory, sorted memory, and audit trail log for some of the most widely used record sizes.  Please note that the HMS software currently only uses the Unsorted Memory Area for code storage, although future plans include Sorted Memory Area support.

| Record Size | Unsorted Memory Area | Sorted Memory Area | Audit Log Records |
| --- | --- | --- | --- |
| 4 | 10240 | 32085 | 16320 |
| 5 | 8777 | 27501 | 16320 |
| 6 | 7680 | 24064 | 16320 |
| 7 | 6826 | 21390 | 16320 |
| 8 | 6144 | 19251 | 16320 |
| 9 | 5585 | 17501 | 15360 |
| 10 | 5120 | 16042 | 14528 |
| 11 | 4726 | 14808 | 13760 |
| 12 | 4388 | 13750 | 13056 |
| 13 | 4096 | 12834 | 12480 |
| 14 | 3840 | 12032 | 11904 |
| 15 | 3614 | 11324 | 11392 |
| 20 | 2792 | 8750 | 9344 |
| 25 | 2275 | 7130 | 7936 |
| 40 | 1462 | 4583 | 5440 |

## APPENDIX B – COMPATIBLE POE SWITCHES

The following POE power inserters have been testing and approved for use with the 8000 controller:

SonicWall	Part No. 01-SSC-5531	Inserts power on unused lines.

Netgear	Part No. FS108P, FS116P	Switches that Inserts power on data lines.

## APPENDIX C – WIEGAND BIT SIZE TABLE

This table shows the number of bits required to encode a specific number into wiegand. This table can also be used to see how many characters are required to decimalize wiegand input fields.

Bits		Decimal Number		 Bits		Decimal Number

1 		1 				33		8,589,934,591

2 		3 				34 		17,179,869,183

3 		7 				35 		34,359,738,367

4 		15 				36 		68,719,476,735

5 		31 				37 		137,438,953,471

6 		63 				38 		274,877,906,943

7 		127 				39 		549,755,813,887

8 		255 				40 		1,099,511,627,775

9 		511 				41 		2,199,023,255,551

10 		1,023 			42 		4,398,046,511,103

11 		2,047 			43 		8,796,093,022,207

12 		4,095 			44 		17,592,186,044,415

13 		8,191 			45 		35,184,372,088,831

14 		16,383 			46 		70,368,744,177,663

15 		32,767 			47 		140,737,488,355,327

16 		65,535 			48 		281,474,976,710,655

17 		131,071 			49 		562,949,953,421,311

18 		262,143 			50 		1,125,899,906,842,623

19 		524,287 			51 		2,251,799,813,685,247

20 		1,048,575 			52 		4,503,599,627,370,495

21 		2,097,151 			53 		9,007,199,254,740,991

22 		4,194,303 			54 		18,014,398,509,481,983

23 		8,388,607 			55 		36,028,797,018,963,967

24 		16,777,215 		56 		72,057,594,037,927,935

25 		33,554,431 		57 		144,115,188,075,855,871

26 		67,108,863 		58 		288,230,376,151,711,743

27 		134,217,727 		59 		576,460,752,303,423,487

28 		268,435,455 		60 		1,152,921,504,606,846,975

29 		536,870,911 		61 		2,305,843,009,213,693,951

30 		1,073,741,823 		62		4,611,686,018,427,387,903

31 		2,147,484,647 		63 		9,223,372,036,854,775,807

32 		4,294,967,295 		64 		18,446,744,073,709,551,615

## APPENDIX D – TESTED COMPATIBLE READERS

Highpower strives to make the Model 3000 as compatible as possible with Wiegand devices from many manufacturers.  In accordance with this goal, we have created our Wiegand interface to automatically detect the transmission speed of any Wiegand device connected.

As a result, we are compiling a list of Wiegand devices that have been tested with the Model 3000.  These devices include the following:

### PROXIMITY READERS

All Wiegand “Pyramid” Reader Heads from Farpointe Data.

Note: These are good readers for most applications.

All Wiegand “Revision E” model readers from AWID (Applied Wireless ID, Inc.)

Note: This brand is common in the security industry.

All Wiegand Readers from HID Corporation.

Note: This is the most common brand in the security industry.

### BAR CODE READERS

All Wiegand models from IBC (International Bar Code, Inc.)

Note: Use the “Smart” models of IBC products when using extended bar codes.

Non-decoded model barcode readers from various brands.

### MAG-STRIPE READERS

All Wiegand models from IBC (International Bar Code, Inc.)

Note: Use the “Smart” models of IBC products when using custom track configurations.

Note to Installers:  If you have successfully used another brand of reader with our controller or are having problems with a particular model of reader, we want to hear from you!  Your comments are appreciated.  Please call us direct at 203-634-3900.